Grid Voltage Fault

Author：胡心怡

Reviewer：Eason

FAQ/ Hybrid INV

Issue introduction

The inverter screen displays:GridVoltFault IE03.

Confirmation of basic information

[Photo] SN numbers of inverters.

Guidance for installer

Step1: Use a multimeter to measure the voltage at the inverter's AC port. In a three-phase system, measure the line voltage.

| Phase voltage on the grid side | Line voltage(line voltage＝√3×Phase voltage) |
| --- | --- |

Step2: Select the correct safety code.

Settings path:Advance setting→Safety

Step3: If none of the above solutions can solve the problem,adjust up grid protection voltage value by 5V

Settings path:Advance setting→Grid Voltage Parameters→OverVoltage_L1(V)

Information check list

If you have completed the above <Guidance for installer>, and the problem is still not solved, please collect the following troubleshooting information and send them to the R&D.

1. [Photo]SN number of the inverter, which should clearly display the registration number.

2.[Photo]Local grid phase and line voltage.

3.[Photo]Inverter safety settings.

4.[Photo]The overvoltage protection values.