BMS Lower Voltage

Alarm Attribute

| Alarm name | Alarm Severity | Alarm Category |
| --- | --- | --- |
| BMS Lower Voltage | General | Battery alarm |

Possible Cause

| Cause ID | Possible Cause |
| --- | --- |
| 1 | Battery cell lower-voltage fault: The voltage of the battery cell is less than 2.85V |

Suggestion

1.Use forced charging mode to recharge the battery. If forced charging is not possible, use the T-BAT-Charger to charge the battery individually.

- 2.If the battery cannot be awakened with charging, provide the completed troubleshooting results to SolaX technical support team through video or images.Including but not limited to:
1) SN number of the inverter.