Cluster Communication Address Repeated

Alarm Attribute

| Alarm name | Alarm Severity | Alarm Category |
| --- | --- | --- |
| Cluster Communication Address Repeated | General | Battery alarm |

Possible Cause

| Cause ID | Possible Cause |
| --- | --- |
| 1 | Battery cluster communication address is repeated. |
| 2 | HS battery three clusters in parallel, two slave clusters have the same ID. |

Suggestion

1. After the fault is reported, the master will reallocate the address and the fault will be restored；

2. Upgrade the firmware to the latest version.If the issue remains,provide the inverter's SN number to the SolaX technical support team for further analysis.