NTC Sample Invalid

Alarm Attribute

| Alarm name | Alarm Severity | Alarm Category |
| --- | --- | --- |
| NTC Sample Invalid | General | Communication alarm |

Possible Cause

| Cause ID | Possible Cause |
| --- | --- |
| 1 | Lead-acid battery temperature sampling fault |
| 2 | External NTC unable to read temperature |

Suggestion

- 1.Check if the battery type in the inverter settings is incorrectly set to lead-acid batteries.

- 2.Check if the external NTC of the lead-acid battery is properly connected.

- 3.Check if the wiring of the NTC communication interface conforms to the requirements in the manual.

- 4.If the issue remains, provide the completed troubleshooting results to SolaX technical support team through video or images.Including but not limited to:
1) SN number of the inverter.
2) Battery type settings.
2)A photo of the NTC communication port, clearly showing the wiring details.