Battery Connection Direction Fault

Alarm Attribute

| Alarm name | Alarm Severity | Alarm Category |
| --- | --- | --- |
| Battery Connection Direction Fault | General Alarm | Inverter alarm |

Possible Cause

| Cause ID | Possible Cause |
| --- | --- |
| 1 | Battery Connection Direction Fault: The power cable connection of the battery is reversed. |

Suggestion

1.Connect the power cables from the inverter to the battery master, but do not connect the other end of the cables to the inverter. Then, use a multimeter to measure the voltage at the cable terminals. If the measurement result is negative, the terminal assembly is incorrect, causing the inverter to detect a reverse battery connection.

2.If the measurement result is positive, update the inverter firmware to the latest version and restart the inverter.

- 3.If the issue remains, provide the completed troubleshooting results to SolaX technical support team through video or images.Including but not limited to:
1) SN number of the inverter.
2)The power cables connecting the inverter to the battery, with emphasis on the terminals connected to the inverter.